Thermal Blanket Design: HT1500MSSiM (HT815C-MSSiM)

Applications: Gas Turbines, Catalytic Converters, Turbine Exhaust Duct, Engine Exhaust Manifolds, Reducer Cones, Mufflers, Expansion Joints, Piping, Fittings, By-Pass Piping and Turbo Charger Casings.

Service: Thermal Blanket Insulation for “High Temperature Engine Exhaust” (temperature above 1100˚F)

Maximum Service Temperature: 1500˚F (815˚C)

Purpose: Thermal Blankets are a CAD designed, CNC produced, high quality pre-engineered insulation system designed to save energy, retain radiant heat, minimize insulation maintenance and improve the surrounding work environment. Thermal Blankets are weather resistant and chemical resistant. Thermal Blankets are flexible and easy to install, remove and reinstall allowing quick access and easy equipment serviceability. The key benefit is “Re-Usability”.

Blanket Components: The Outer Jacketing consists of a layer of Stainless Steel Type 304 Knitted Wire Mesh 0.11” Dia. @ 16ft²/lb (0.28 mm Dia. @ 3.3 m²/kg) and 577g/m² (17.0 oz/yd²) Silicone Impregnated Fiberglass Cloth. The inner jacket consists of a layer of 427g/m² (18.0oz/yd²) Ceramic Silica Cloth with an outer layer of Stainless Steel Type 304 Knitted Wire Mesh (0.28 mm Dia. @ 3.3 m²/kg). The Insulation Material is a 128 kg/m3 (8 lb/ft3) Ceramic Needled Fiber Mat. The Mat is encapsulated by the Stainless Mesh, Silicone Fiberglass Cloth, Stainless Sheet Foil and Stainless Mesh, then stapled together, producing a “Self-Contained System”. The Blanket includes Integral Fasteners for easy install.

Blanket Construction: Blanket construction shall be a “Stapled Construction”. Outer jacket materials will be drawn down, to match at the inner or outer jacket edge. Jacketing will be folded under and stapled with 3/8” (0.95 cm) Monel bevel point staples at the outer edge seam. Staples are to follow the inner or outer jacket edge with at most 1” (2.5 cm) spacing between staples. No “On-Site Fabrication” to assure high quality.

ID Plate: For easy identification and location, a stainless steel or aluminum name plate tag is riveted to each blanket piece. 1/8” (0.32CM) embossed lettering shows location, description, size, pressure rating, Work Order, Manufacturing Date and Tag Number Sequence. Each blanket will include an ID Plate.

Design Approach: Thermal Blankets will be custom fit to match each specific component geometry. Standard “Generic Designs” are not acceptable. Thermal Blankets will be a self-contained insulation system with an integral fastener to allow for easy access, removal and re-installation.

Blanket Weight: Any one piece will not exceed 40lbs (18 kg) in weight.

Blanket Overlap: Thermal blanket will extend beyond the mating flange onto existing insulation for a minimum of 2” (5 cm). Fitting sizes 6” (15 cm) or more must have a minimum 4” (10 cm) overlap. Open gaps are not acceptable.

Leak Accommodations:  To accommodate a leak and detect its origin, blankets will have a low point stainless steel/brass drain grommet or the design will include a low point blanket seam..

CAD / CNC Requirement: Thermal Blanket Insulation will require CAD Drawing Submittals to assure accuracy of design. Upon receipt of project contract, each item must be field measured, tagged and “Custom Fitted” to assure a quality fit and finish. All blankets are to be CAD designed / CNC produced to assure the highest quality, precise fit and electronic CAD filing retrieval for future replacement.

Manufacture Origin:  Blanket & Blanket Components must be made in the U.S.A.

SELECT YOUR: FASTENER

STANDARD FASTENER “WIRETWISTS”: A stainless steel wire 20 Gauge (0.5 mm²) will be doubled up and twisted in a spiral fashion, with a minimum of 5-7 twists/Inch (2-3 twists/CM). Wiretwist length will be 16” (40 cm). The Wiretwist will be secured to the lacing pin at the pin stem. Pin stems will be 14 gauge (2.5 mm²). Wiretwists will be spaced at most 6” (15 cm) on center along closing seams with matching lacing pins for securing.

OPTIONAL FASTENER: Metal Spring Tensioner – 5/16” Dia.(7.94mm) - 3.8 lb/in (0.07 kg/mm) Rating – 2 ½” (6.35cm) Length, combined with 2 each 1 ¼” (3.2cm) Diameter stainless steel split rings, fastened to the blanket edge, 2” (5cm) from the blanket edge. The spring tensioner will be secured to the lacing pin at the spring ring edge. Pin stems will be 14 gauge (2.5 mm²). The Metal Spring Tensioner will be spaced at most 6” (15 cm) on center along closing seams with matching lacing pins for securing. The Metal Spring Tensioner will be positioned between the outer jacketing & outer layer of the insulation.

Blanket Design Warranty: Thermal Blankets will accommodate vibration probes, gauges, tubing, piping, brackets, etc. and fit correctly for optimum performance as per the design specification provided in the quotation process. In addition, for 18 months thermal blanket manufacturer will cover the cost of replacing the blanket should the failure be due to premature degradation of any component utilized in the blanket construction, as well as any defects due to poor workmanship.

| Blanket Thickness Surface Temperature Reference: |
| --- |
| Operating Temperature | Thickness | Surface Temperature | Thickness | Surface Temperature | Thickness | Surface Temperature |
| 538˚ C (1000˚ F) | 50 mm (2") | 87.4˚ C (189.4˚ F) | 65 mm (2.5") | 77.3˚ C (171.2˚ F) | 80 mm (3.0") | 70.1˚ C (158.1˚ F) |
| 482˚ C (1100˚ F) | 65 mm(2.5") | 76.1˚ C (169˚ F ) | 80 mm (3.0") | 68.9˚ C (156.0˚ F ) | 88 mm (3.5") | 61.1˚ C (142.0˚ F ) |
| 538˚ C (1200˚ F) | 50 mm(2") | 88˚ C (191˚ F ) | 80 mm (3.0") | 72.0˚ C (161.0˚ F ) | 88 mm (4.0") | 62˚ C (144.0˚ F ) |
| 760˚ C (1400˚ F) | 50 mm(2") | 107˚ C (225˚ F ) | 80 mm (3.0") | 86˚ C (187˚ F ) | 102mm(4.0") | 74˚ C (165.0˚ F ) |
| 871˚ C (1600˚ F) | 50 mm(2") | 128˚ C (262˚ F ) | 80 mm (3.0") | 102˚ C (216˚ F ) | 102mm(4.0") | 87˚ C (189.0˚ F ) |
| * The above referenced Cold Face Surface Temperatures should be used as guidelines for blanket insulation thickness design. |
| * The Cold Face Surface Temperature of the blanket should approach surrounding ambient temperature conditions. |
| * The economic thickness of the blanket should consider blanket cost, thermal performance and blanket design constraints. |
| * Heat Loss Calculations are based on a 21.1˚ C (70˚ F) ambient temperature using a flat surface condition. |

SELECT YOUR: Testing Requirements

ASTM C 335	Standard Test Method for Steady-State Heat Transfer Properties of Pipe Insulation.
ASTM E 1222 – 90	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation – USA
ISO 15665	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation – Int’l
ASTM C 1045 – 07	Standard Practice for Calculating Thermal Transmission Properties under steady state conditions
UL 1709		Standard Fire Test of Protection Materials for MOV / Structural Steel
ASTM E-84-17	Surface Burning Characteristics of Building Materials (Flame Spread & Smoke)
ASTM E-136	Combustion Characteristics of Building Materials / Fire Test Response
ASTM D3787	Burst Strength Evaluation for ASTM F1138 – Spray Shield Compliance