Acoustic Blanket Design: LT250A-VP (LT121C-A-VP)

Applications: Shannon Acoustic Blanket Applications include; Compressor Housings, Motors, Blowers, Rotary Chillers, Gear Boxes, Valves, Piping and Fittings, Pump Housings and Fan Housings.

Service: This design is to act as a Thermal/Acoustic Noise Barrier addressing “Radiant Noise”

Maximum Service Temperature: 250˚F (121˚C)

Purpose: Shannon Acoustic Blankets are a CAD designed, CNC produced, high quality, engineered insulation system designed to reduce noise levels, minimize insulation maintenance and improve the surrounding work environment. Shannon Acoustic Blankets are weather and chemical resistant. Shannon Acoustic Blankets are flexible, easy to install, remove and reinstall, allowing quick and easy access for serviceability. The key benefit is “Re-Usability”.

Acoustic Performance: 	4 – 15 DBA Reduction Overall

Finished Surface Mass:	1.7lb/ft² (8.3 kg/m²) to 3.7lb/ft² (18.1 kg/m²)

Product Components: Outer/Inner Jacketing – 18.0oz/yd² (611g/m²) Vinyl Coated Polyester Cloth. Mass Loaded Vinyl “Reflector” – 1.0lb/ft²-2.0lb/ft² (4.9kg/m²-9.8kg/m²). Insulation Core “Absorber” - 11lb/ft3 (176.2 kg/m3) Fiberglass Needled Mat-Type “E” Fiber. The Fiberglass Mat is encapsulated by the Outer/Inner Jacketing and sewn together, producing a “Self-Contained Blanket System”. The Blanket System includes Integral Fasteners for install & removal.

Blanket Construction: Blanket construction shall be a “Double Sewn” lock stitch with a minimum 7 stitches/inch (2.8 stitches/CM). Blanket edges will have a tri-fold Vinyl Polyester cloth binding. No raw cut jacket edge will be exposed. Stitching will be Nylon or Polyester thread. No “On-Site Fabrication” to assure high quality.

ID Plate: For easy identification and location, a stainless steel or aluminum name plate tag is riveted to each blanket piece.

Design Approach: Blankets will be custom fit to match each specific component geometry. “Generic Designs” are not acceptable. Blankets will be a “Self-Contained” insulation system with an integral fastener to allow for easy access, removal and re-installation.

Blanket Weight: Any one piece will not exceed 40lbs (18 kg) in weight.

Blanket Overlap: Blanket will extend beyond the mating flange onto existing insulation for a minimum of 2” (5CM). Fitting sizes 6” (15cm) or more must have a minimum 4” (10CM) overlap. Open gaps are not acceptable.

Leak Accommodations:  To accommodate a leak and detect its origin, blankets will have a low point stainless steel/brass drain grommet or the design will include a low point blanket seam.

CAD / CNC Requirement: Acoustic Blanket Insulation will require CAD Drawing Submittals to assure accuracy of design. Upon receipt of project contract, each item must be field measured, tagged and “Custom Fitted” to assure a quality fit and finish. All blankets are to be CAD designed / CNC produced to assure the highest quality, precise fit and electronic CAD filing retrieval for future replacement.

Manufacture Origin:  Blanket & Blanket Components must be made in the U.S.A.

STANDARD FASTENER:

WIRETWIST / Velcro® Vinyl Flap: Fabric Extended Jacketing Flaps with an integral Mass Loaded Vinyl are secured by the utilization of Hook/Loop (Velcro®) fasteners. A 2” (5cm) wide section of the (Velcro®) Hook will be stitched to the outer surface of the blanket. A 2” (5cm) wide section of the (Velcro®) Loop will be aligned and stitched on the mating inner surface of an extended 2”(5cm) Mating Seam or 2 ½”(6.4cm) Closure Seam Jacketing Flap.

A stainless steel wire 20 Gauge (0.5 mm Dia.) will be doubled up and twisted in a spiral fashion, with a minimum of 5-7 twists/Inch (2-3 twists/cm). Wiretwist length will be 16” (40 cm). The Wiretwist will be secured to the lacing pin at the pin stem. Pin stems will be 14 gauge (2.5 mm2). Wiretwists will be spaced at most 6” (15 cm) on center along closing seams with matching lacing pins for securement.

Optional Fastener:

1.) Lacing Pins - Stainless Steel Type 304 Lacing Pins. These pins will be 14 gauge. Location of pins on the blanket will be 2” (5cm) or more from blanket edge and 8” (20cm) or less from centerline to centerline along the blanket edge.

2.) Optional: Metal “D” Ring Strap with Velcro Tab: A three layer fabric strap is double sewn. One strap is a 12” (30CM) long pull-down strap, the other is a 3” (8CM) long stationary strap. Both straps are stitched to the outer jacketing of the blanket. The stationary strap includes a metal “D” Ring measuring 1”-1.5” wide (2.5-3.8CM). This is placed ½” (1.25CM) from the closing seam edge. The pull-down strap is placed 2” (5CM) in from the closing seam edge. Both matching straps are spaced along the closing seam edge no greater than 6” (15CM) apart. The pull-down strap includes hook-and-loop Velcro®, measuring at least 1” (2.5CM) wide by 5” (12.7CM) long, and is perimeter stitched to the strap surface. All closing seams have a 1.5” (3.8CM) extended fabric flap, which is placed along the stationary strap side of the closing seam.

Blanket Design Warranty: Blankets will accommodate vibration probes, gauges, tubing, piping, brackets, etc. and fit correctly for optimum performance as per the design specification provided in the quotation process. In addition, for 18 months thermal blanket manufacturer will cover the cost of replacing the blanket should the failure be due to premature degradation of any component utilized in the blanket construction, as well as any defects due to poor workmanship.

SELECT YOUR: Thickness, Surface Mass & Noise Reduction Range

| Thickness | Surface Mass | Noise Reduction Range |
| --- | --- | --- |
| 1” (2.5CM) | 1.8 lb/ft² to 2.8 lb/ ft² (8.8-13.7kg/m²) | 1.5 DBA to 6 DBA Reduction |
| 1 ½” (3.8CM) | 2.2 lb/ ft² to 3.2 lb/ ft² (10.7-15.6kg/m²) | 4 DBA to 8 DBA Reduction |
| 2” (5CM) | 2.6 lb/ ft² to 3.6 lb/ ft² (12.7-17.6kg/m²) | 5 DBA to 10 DBA Reduction |
| 2 ½” (6.4CM) | 3.0 lb/ ft² to 4.0 lb/ ft² (14.7-19.5kg/m²) | 7 DBA to 13 DBA Reduction |

* The above referenced Acoustic Performance should be used as a guideline for blanket insulation thickness design.

* The Acoustic Performance of the blanket should be bench marked against the ambient noise condition.

* The economic thickness of the blanket should be considered in selection of a target reduction with consideration  to blanket design constraints.

* Contact Shannon Enterprises for guidance in selection, as the historical performance of each application varies significantly.

SELECT YOUR: Testing Requirements

ASTM C 335	Standard Test Method for Steady-State Heat Transfer Properties of Pipe Insulation.

ASTM E 1222 – 90	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation - USA

ISO 15665	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation – Int’l

ASTM C 1045 – 07	Standard Practice for Calculating Thermal Transmission Properties under steady state conditions

UL 1709		Standard Fire Test of Protection Materials for MOV / Structural Steel

ASTM E-84-17	Surface Burning Characteristics of Building Materials (Flame Spread & Smoke)

ASTM E-136	Combustion Characteristics of Building Materials / Fire Test Response

ASTM D3787	Burst Strength Evaluation for ASTM F1138 – Spray Shield Compliance