Thermal Blanket Design: LT450TT (LT232C-TT)

Applications: Gate, Globe, Ball, Butterfly, Control and Wafer Valves, Flanges, Pumps, Instrumentation, Equipment Heads, any and all complex surfaces.

Service: Thermal Blanket Insulation for “Low Temp Thermal Process”

Maximum Service Temperature: 450˚F (232˚C)

Purpose: Thermal Blanket Insulation is a CAD designed, CNC produced, high quality pre-engineered insulation system designed to save energy, capture radiant heat, minimize insulation maintenance and improve the surrounding work environment. Shannon Thermal Blanket is capable of withstanding severe indoor and outdoor environments. Thermal Blanket is flexible, easy to install, remove and reinstall, allowing quick access and easy equipment serviceability. The key benefit is “Re-Usability”.

Blanket Components: The Outer and Inner Jacket is a 16.5oz/yd² (560g/m²) PTFE Teflon® Impregnated Fiberglass Cloth. The Insulation Material is an 11lb/CF (176.2 kg/m3) Fiberglass Needled Mat-Type “E” Fiber. The Fiberglass Mat is encapsulated by the PTFE Teflon ® Impregnated Fiberglass Cloth and sewn together, producing a “Self-Contained Blanket System”. The Shannon Thermal Blanket includes Integral Fasteners for install & removal.

Blanket Construction: Blanket construction shall be a “Double Sewn” lock stitch with a minimum 7 stitches/inch (2.8 stitches/CM). Blanket edges will have a tri-fold PTFE Teflon® Fiberglass cloth binding. No raw cut jacket edge will be exposed. Stitching will be Nylon or Pure PTFE thread. No “On-Site Fabrication” to assure high quality.

ID Plate: For easy identification and location, a stainless steel or aluminum name plate tag is riveted to each blanket piece.

Design Approach: Thermal Blankets will be custom fit to match each specific component geometry. “Generic Designs” are not acceptable. Thermal Blankets will be a self-contained insulation system with an integral fastener to allow for easy access, removal and re-installation.

Blanket Weight: Any one piece will not exceed 40lbs (18 KG) in weight.

Blanket Overlap: Thermal blanket will extend beyond the mating flange onto existing insulation for a minimum of 2”(5CM). Fitting sizes 6” or more must have a minimum 4” (10CM) overlap. Open gaps are not acceptable.

Leak Accommodations:  To accommodate a leak and detect its origin, blankets will have a low point stainless steel/brass drain grommet or the design will include a low point blanket seam.

CAD / CNC Requirement: Thermal Blanket Insulation will require CAD Drawing Submittals to assure accuracy of design. Upon receipt of project contract, each item must be field measured, tagged and “Custom Fitted” to assure a quality fit and finish. All blankets are to be CAD designed / CNC produced to assure the highest quality, precise fit and electronic CAD filing retrieval for future replacement.

Manufacture Origin:  Blanket & Blanket Components must be made in the U.S.A.

SELECT YOUR: FASTENER

STANDARD FASTENER “WIRETWISTS”: A stainless steel wire 20 Gauge (0.5 mm2) will be doubled up and twisted in a spiral fashion, with a minimum of 5-7 twists/Inch (3-5 twists/CM. Wiretwist length will be 16” (40 CM). The Wiretwist will be secured to the lacing pin at the pin stem. Pin stems will be 14 gauge (2.5 mm2). Wiretwists will be spaced at most 6” (15 CM) on center along closing seams with matching lacing pins for securing.

FASTENING OPTIONS:

1.) Velcro® Flaps: Jacketing flaps are secured closed by the utilization of Hook/Loop (Velcro®) fasteners. A 2” (5CM) wide section of the Hook portion of the fastener will be stitched to the outer surface of the blanket. A 2” (5CM) wide section of the Loop portion will be aligned and stitched on the mating inner surface of an extended 2” (5CM) or 2 ½” (6.4CM) jacketing flap.

2.) Metal “D” Ring Strap with Velcro Tab: A three layer fabric strap is double sewn. One strap is a 12” (30CM) long pull-down strap, the other is a 3” (8CM) long stationary strap. Both straps are stitched to the outer jacketing of the blanket. The stationary strap includes a metal “D” Ring measuring 1”-1.5” wide (2.5-3.8CM). This is placed ½” (1CM) from the closing seam edge. The pull-down strap is placed 2” (5CM) in from the closing seam edge. Both matching straps are spaced along the closing seam edge no greater than 6” (15CM) apart. The pull-down strap includes hook-and-loop Velcro®, measuring at least 1” (2.5CM) wide by 5” (12.7CM) long, and is perimeter stitched to the strap surface. All closing seams have a 1.5” (3.8CM) extended fabric flap, which is placed along the stationary strap side of the closing seam.

3.) Side Release Buckles: The blanket fasteners will be 1” or 1.5” (2.5-3.8CM) Polypropylene Side Release Buckles with 1”-1.5” (2.5-3.8CM) wide fabric straps. A tri-fold 1’-1.5” (2.5-3.8CM) wide belt will be sewn together utilizing PTFE 3 ply thread. A row of stitching, along each side of the belt will be parallel for the entire length. The Buckle strap will be a minimum of 5” (12.7CM) long and will be box stitched to the outer surface for a minimum of 3” (8CM) in length. A matching pull strap will be box stitched on the outer jacket surface and will match up to the Buckle Strap. The pull strap will be a minimum of 12” (30 CM) long.

Blanket Design Warranty:

Thermal Blankets will accommodate vibration probes, gauges, tubing, piping, brackets, etc. and fit correctly for optimum performance as per the design specification provided in the quotation process. In addition, for 18 months thermal blanket manufacturer will cover the cost of replacing the blanket should the failure be due to premature degradation of any component utilized in the blanket construction, as well as any defects due to poor workmanship.

SELECT YOUR: Testing Requirements

ASTM C 335	Standard Test Method for Steady-State Heat Transfer Properties of Pipe Insulation.

ASTM E 1222 – 90	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation - USA

ISO 15665	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation – Int’l

ASTM C 1045 – 07	Standard Practice for Calculating Thermal Transmission Properties under steady state conditions

UL 1709		Standard Fire Test of Protection Materials for MOV / Structural Steel

ASTM E-84-17	Surface Burning Characteristics of Building Materials (Flame Spread & Smoke)

ASTM E-136	Combustion Characteristics of Building Materials / Fire Test Response

ASTM D3787	Burst Strength Evaluation for ASTM F1138 – Spray Shield Compliance