Thermal Blanket Design: MT800SGM (MT427C-SGM)

Applications:  Gate Valves, Small Steam Turbines, Globe Valves, Flanges, Expansion Joints, Feed Water Pumps and Pressure Reducing Stations, Boiler Components. Markets include; Steam, District Heating, Boiler Rooms and Power Plants.

Service: Thermal Blanket Insulation for “Mid Temperature High Pressure Steam Process”

Maximum Service Temperature: Steam Systems above 550F (288˚C). This design is to act as a Thermal Barrier with a maximum service temperature of 800˚F (427˚C).

Purpose: Thermal Blankets are a CAD designed, CNC produced, high quality pre-engineered insulation system designed to save energy, retain radiant heat, minimize insulation maintenance and improve the surrounding work environment. Thermal Blankets are weather and chemical resistant. Thermal Blankets are flexible, easy to install, remove and reinstall allowing quick and easy serviceability. The key benefit is “Re-Usability”.

Blanket Components: The Outer Jacket is a 17.0 oz/yd² (577g/m²) Silicone Impregnated Fiberglass Cloth. The inner jacket consists of a layer of Stainless Steel Knitted Wire Mesh on the outside, encasing a layer of 18.0 oz/yd² (611g/m²) Plain Fiberglass Cloth. The Insulation Core Material is an 11 lb/ft3 (176.2 kg/m3) Fiberglass Needled Mat-Type “E” Fiber. The Fiberglass Mat is encapsulated by the outer Silicone Fiberglass Cloth, inner Plain Fiberglass Cloth and Stainless Steel Knitted Wire Mesh, sewn together, producing a “Self-Contained Blanket System”. The Shannon Thermal Blanket System includes Integral Fasteners for install & removal.

Blanket Construction: Blanket construction shall be a “Double Sewn” lock stitch with a minimum 7 stitches/inch (2.8 stitches per CM). Raw jacket edges will have a tri-fold Silicone Fiberglass Cloth binding. No raw cut jacket edge will be exposed. Stitching will be pure PTFE, Nylon and or Stainless Steel thread. Monel metal bevel point staples 3/8” (0.95CM) wide, must follow the outer jacket edge for re-enforcement and to be spaced no greater than 1” (2.5 CM) apart on center. Staples will penetrate the binding edge. No “On-Site Fabrication” to assure high quality.

ID Plate: For easy identification and location, a stainless steel or aluminum name plate tag is riveted to each blanket piece.

Design Approach: Thermal Blankets will be custom fit to match each specific component geometry. “Generic Designs” are not acceptable. Thermal Blankets will be a self-contained insulation system with an integral fastener to allow for easy access, removal and re-installation.

Blanket Weight: Any one piece will not exceed 40lbs (18 KG) in weight.

Blanket Overlap: Thermal blanket will extend beyond the mating flange unto existing insulation for a minimum of 2”(5 CM). Fitting sizes 6” (15CM) or more must have a minimum 4” (10CM) overlap. Open gaps are not acceptable.

Leak Accommodations:  To accommodate a leak and detect its origin, blankets will have a low point stainless steel or brass drain grommet or the design will include a low point blanket seam.

CAD / CNC Requirement: Thermal Blanket Insulation will require CAD Drawing Submittals to assure accuracy of design. Upon receipt of project contract, each item must be field measured, tagged and “Custom Fitted” to assure a quality fit and finish. All blankets are to be CAD designed / CNC produced to assure the highest quality, precise fit and electronic CAD filing retrieval for future replacement.

Manufacture Origin:  Blanket & Blanket Components must be made in the U.S.A.

SELECT YOUR: FASTENER

STANDARD FASTENER “WIRETWISTS”: A stainless steel wire 20 Gauge (0.5 mm2) will be doubled up and twisted in a spiral fashion, with a minimum of 5-7 twists/Inch (2-3 twists/CM). Wiretwist length will be 16” (40 CM). The Wiretwist will be secured to the lacing pin at the pin stem. Pin stems will be 14 gauge (2.5 mm2). Wiretwists will be spaced at most 6” (15 CM) on center along closing seams with matching lacing pins for securing.

Optional Fasteners:

1.) Metal “D” Ring Strap with Velcro Tab: A three layer fabric strap is double sewn. One strap is a 12” (30CM) long pull-down strap, the other is a 3” (8CM) long stationary strap. Both straps are stitched to the outer jacketing of the blanket. The stationary strap includes a metal “D” Ring measuring 1”-1.5” wide (2.5-3.8CM). This is placed ½” (1CM) from the closing seam edge. The pull-down strap is placed 2” (5CM) in from the closing seam edge. Both matching straps are spaced along the closing seam edge no greater than 6” (15CM) apart. The pull-down strap includes hook-and-loop Velcro®, measuring at least 1” (2.5CM) wide by 5” (12.7CM) long, and is perimeter stitched to the strap surface. All closing seams have a 1.5” (3.8CM) extended fabric flap, which is placed along the stationary strap side of the closing seam.

2.) Side Release Buckles: The blanket fasteners will be 1” or 1.5” (2.5-3.8CM) Polypropylene Side Release Buckles with 1”-1.5” (2.5-3.8CM) wide fabric straps. A tri-fold 1’-1.5” (2.5-3.8CM) wide belt will be sewn together utilizing PTFE 3 ply thread. A row of stitching, along each side of the belt will be parallel for the entire length. The Buckle strap will be a minimum of 5” (12.7CM) long and will be box stitched to the outer surface for a minimum of 3” (8CM) in length. A matching pull strap will be box stitched on the outer jacket surface and will match up to the Buckle Strap. The pull strap will be a minimum of 12” (30 CM) long.

| Blanket Thickness Surface Temperature Reference: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operating Temperature | Thickness | Surface Temperature | Thickness | Surface Temperature | Thickness | Surface Temperature |
| 232˚ C (450˚ F) | 25 mm( 1") | 57.2˚ C (135.1˚ F) | 40 mm (1.5") | 47.8˚ C (118.0˚ F) | 50 mm (2") | 42.3˚ C (108.2˚ F) |
| 260˚ C (500˚ F) | 25 mm( 1") | 62.5˚ C (144.5˚ F) | 40 mm (1.5") | 51.7˚ C (125.1˚ F) | 50 mm (2") | 45.5˚ C (113.9˚ F) |
| 287.8˚ C (550˚ F) | 25 mm( 1") | 67.9˚ C (154.2˚ F) | 40 mm (1.5") | 55.8˚ C (132.4˚ F) | 50 mm (2") | 48.9˚ C (119.9˚ F) |
| 315.6˚ C (600˚ F) | 25 mm( 1") | 72.5˚ C (162.5˚ F) | 40 mm (1.5") | 59.7˚ C (139.5˚ F) | 50 mm (2") | 52.2˚ C (126.0˚ F) |
| 343.3˚ C (650˚ F) | 25 mm( 1") | 79.4˚ C (175.0˚ F) | 40 mm (1.5") | 64.4˚ C (148.0˚ F) | 50 mm (2") | 56.1˚ C (133.0˚ F) |
| 371˚ C (700˚ F) | 40 mm(1.5") | 69.2˚ C (156.5˚ F) | 50 mm (2") | 59.8˚ C (139.6˚ F) | 65 mm (2.5") | 53.6˚ C (128.4˚ F) |
| 427˚ C (800˚ F) | 40 mm(1.5") | 79.2˚ C (174.6˚ F) | 50 mm (2") | 68.1˚ C (154.5˚ F) | 65 mm (2.5") | 60.7˚ C (141.2˚ F) |
| * The above referenced Cold Face Surface Temperatures should be used as guidelines for blanket insulation thickness design. |
| * The Cold Face Surface Temperature of the blanket should approach surrounding ambient temperature conditions. |
| * The economic thickness of the blanket should consider blanket cost, thermal performance and blanket design constraints. |
| * Heat Loss Calculations are based on a 21.1˚ C (70˚ F) ambient temperature using a flat surface condition. |  |

Blanket Design Warranty:

Thermal Blankets will accommodate vibration probes, gauges, tubing, piping, brackets, etc. and fit correctly for optimum performance as per the design specification provided in the quotation process. In addition, for 18 months thermal blanket manufacturer will cover the cost of replacing the blanket should the failure be due to premature degradation of any component utilized in the blanket construction, as well as any defects due to poor workmanship.

SELECT YOUR: Testing Requirements

ASTM C 335	Standard Test Method for Steady-State Heat Transfer Properties of Pipe Insulation.

ASTM E 1222 – 90	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation - USA

ISO 15665	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation – Int’l

ASTM C 1045 – 07	Standard Practice for Calculating Thermal Transmission Properties under steady state conditions

UL 1709		Standard Fire Test of Protection Materials for MOV / Structural Steel

ASTM E-84-17	Surface Burning Characteristics of Building Materials (Flame Spread & Smoke)

ASTM E-136	Combustion Characteristics of Building Materials / Fire Test Response

ASTM D3787	Burst Strength Evaluation for ASTM F1138 – Spray Shield Compliance